TENDER SPECIFICATIONS

The “ERP” application consists of the following elements:

• ERP-UB. Protection Relays Test Base Unit.

The Protection Relays Test Base Unit, “ERP-UB”, has been designed for comprehensive investigations into the theory and practice of electrical power system protection.

This unit is common for the relays type “ERP” and can use one or more relays.

Floor-standing unit, mounted in anodized aluminum frame and panels of painted steel, enabling wide range of protection relay investigations.

It uses genuine industrial application relays, not simulations, with full range of safety features incorporated throughout.

Diagrams on the unit enable students to set up and perform practices and experiments with minimal supervision.

Comprehensive controls, transformers, supplies and instrumentation.

Modern, ergonomic and practical design which includes desk space for users or students to work on, and mounting area for relays.

It is supplied with relay support software.

Selection of up-to-date numerical protection relays, specially adapted for educational use (see required and recommended relays).

This unit consists of this main parts:

Main connections, control and measurement board:

This board has two parts: left hand, right hand and common emergency stop switch in the centre of them.

Elements of the board left hand part:

Input/output signals exchange connector and relay trip indicator.

Fixed three-phase voltage output terminals.

Power supply security connection key switch.

Second fixed three-phase voltage output terminals.

Variable three-phase voltage output terminals. (0 – 400 VAC).

Measurements power analyzer.

Variable three-phase current output terminals. (0 – 10 Amp).

Six current transformers with transformation relation 50/5 CT= 10.

Three voltage transformers with transformation relation:

Primary= 400/√3.

Secondary= 110/√3.

PT= primary/secondary= 3.64.

Emergency stop switch.

Elements of the board right hand part:

Input/ouput signals exchange connector and relay trip indicator.

Fixed three-phase voltage output terminals.

Power supply security connection key switch.

Second fixed three-phase voltage output and transformer input terminals.

Transformer primary voltage tap changer selector.

Transformer secondary connection type selector: star/delta.

Measurements power analyzer.

Transformer three-phase voltage output terminals.

Load connection type selector: star/delta.

Delta and star load terminal connectors.

Six current transformers with transformation relation 10/5 CT= 2.

Three voltage transformers with transformation relation:

Primary= 400/√3.

Secondary= 110/√3.

PT= Primary/Secondary= 3.64.

Emergency stop switch.

Three-phase voltage regulation dial selector.

Three-phase load regulation dial selector.

Unit power supply and protection:

Three-phase power supply.

Current source overload thermal protection.

Left board part magnetoghermal protection.

Right board part magnetothermal protection.

Left board part voltage measurement circuit protection.

Right board part voltage measurement circuit protection.

Control circuits magnetothermal protection.

Dimensions: 1250 x 800 x 2000 mm aprox. (49.21 x  31.49 x 78.74 inches approx.). Weight: 400 kg aprox. (881 pounds approx.).

Required elements to operate with “ERP-UB” (Not included):

• ERP-MF. Fault Injection.

It enables the injection of different types of short circuits, in any point of the Protection Relays Test Base Unit, “ERP-UB”. It is required line unit, directly or through a variable pure resistive element. Employing this element we can analyze the different protection elements functionality with different fault intensity.

The short-circuit injection possibility are:

Three-pole short-circuit.

Two-pole short-circuit.

Two-pole ground short-circuit.

Single-pole ground short-circuit.

Test circuits:

Configurable power transformer test circuit.

Configurable load test circuit.

Configurable measurement test circuit.

Relays test area.

Dimensions: 490 x 330 x 310 mm approx. (19.29 x 12.99 x 12.20 inches approx.). Weight: 10 kg approx. (22 pounds approx.).

• AE1. Transmission Lines Simulation Unit.

This unit represents basic concepts of the electric energy high voltage three-phase transmission lines operation. It simulates a value modifying concentrated parameter line that allows different configurations and consists on three conductor line (L1, L2, L3) and a neutral or return line (N).

Each of the phases is represented, following the concentrated parameters theoretical model, through a resistance series association and inductance, along with a parallel association between each one of them in a capacitance effect.

A way to reduce the earth short circuit current is to have impedance in the neutral to ground connections. This impedance has no repercussion in the normal functioning of the network but they introduce a repercussion in the increase of 3 x Zo (impedance on the zero sequence component), which reduces the short circuit current.

The return line is simulated through small value impedance that has a resistive inductive characteristic. To simplify the effect, being a negligible inductance, it will be simulated with a pure 10 Ω resistance.

The phases have two terminals at the input and two at the output, and they are connected at the interior. Through one of them the unit will be supplied. Through the last one the natural circuit will continue to the load module, the busbar module, the transformer, etc. There are additional terminals for assembly of protection relay or other parallel configurations.

The supply of this unit will be done through line terminals (L1, L2, L3) and the neutral (N) through a 400 V three-phase supply and it will be controlled by any power circuit breaker of 4 poles placed between the supply and the lines section.

In the phases we can distinguish different resistance and inductance values, being able to simulate different length transport lines.

The resistive part is formed by two resistance values of 15 Ω and 33 Ω, with the possibility of making parallel series connections between them, obtaining two additions resistive values of 10.31 Ω and 48 Ω.

The inductive part consists on a multistage coil of despicable resistance. In which it is possible to choose one of the following values: 33 mH, 78 mH, 140 mH, 193 mH, 236 mH.

The capacitive part will be divided into capacitance between conductors and capacitance between line and ground.

The capacitance between conductors is simulated with a pair of capacitors at the beginning and at the end of the line with different values: 0.5 µF and 1 µF for each conductor.

The capacitance between conductor and ground is 1 µF and 2 µF, also at the beginning and at the end of the line.

With all these values it is possible to simulate a great number of line configurations, beginning with different line distances with different types of conductor, through the unbalanced lines with different conductors groups (simplex, duplex, triplex and cuadruplex). At the same time it is possible to simulate transient state with different short circuits injection using the fault injection.

This unit is protected with a ground connection that comes from the metallic frame and that is accessible through a terminal in the front of the unit.

Dimensions: 490 x 450 x 470 mm aprox. (19.29 x 17.71 x 18.50 inches approx.). Weight: 20 kg aprox. (44 pounds approx.).

Additional recommended elements (at least one) for a greater functionality of the “ERP-UB” (Not included):

• ERP-PDF. Differential Protection Relay.

The Differential Protection Relay, ”ERP-PDF”, is used with Protection Relays Test Base Unit, “ERP-UB”, to enable investigations into protection of transformers, autotransformers, generators, busbar and other apparatus with two windings.

It enables a wide range of test and investigations and it demonstrates the latest relay technology.

It demonstrates the characteristics of three-phase differential protection.

Modern and robust enclosure steel box with carrying handles.

Modern industrial application differential protection relay presented in an educational and teaching format.

The connections are via safety sockets.

The main functions:

| Eight Overcurrent Elements for Winding 1 | Instantaneous | Definite Time | Inverse Time |
| --- | --- | --- | --- |
| Phase | 50P1H | 50P1 | 51P1 |
| Negative Sequence |  | 50Q1 | 51Q1 |
| Residual | 50N1H | 50N1 | 51N1 |
| Eight Overcurrent Elements for Winding 2 | Instantaneous | Definite Time | Inverse Time |
| Phase | 50P2H | 50P2 | 51P2 |
| Negative Sequence |  | 50Q2 | 51Q2 |
| Residual | 50N2H | 50N2 | 51N2 |
| Setting Ranges, 5 A Model, (A secondary) | OFF, (0.5-80) | OFF, (0.5-80) | OFF, (0.5-16) |

Selogic control equations.

Event reports.

ASCII. Binary, and distributed port switch communications.

Phase, ground, negative-sequence, differential and harmonic metering.

Restrained and unrestrained differential elements.

Second and fourth harmonic restraint.

Fifth harmonic and DC blocking.

CT and transformer connection compensation.

Connection to the primary and secondary windings of the circuit experimental via current transformers with ratio to suit the inputs of the relay. This provides an effective demonstration of the effect of current and voltage transformer ratio, connection and rating on protective relays.

Accuracy: +- 5%.

Current: 5 A (AC).

Frequency: 50 or 60 Hz.

Operating time: typically 10 ms to 25 ms.

Dimensions: 490 x 330 x 310 mm approx. (19.29 x 12.99 x 12.20 inches approx.). Weight: 10 kg approx. (22 pounds approx.).

• ERP-MA. Feeder Management Relay.

The Feeders Management Relay, ”ERP-MA”, is used with the Protection Relays Test Base Unit, “ERP-UB”, to enable investigations into protection and monitoring of overhead lines, underground cables and feeders.

It enables a wide range of test and investigations and it demonstrates the latest relay technology.

Modern and robust enclosure (steel box) with carrying handles.

Modern industrial application feeder management relay presented in an educational and teaching format.

The connections are via safety sockets.

The main functions:

Four levels of phase instantaneous overcurrent element (50P).

Four levels of negative-sequence overcurrent element (50Q).

Four levels of residual overcurrent element (50G).

Four levels of neutral overcurrent element (50G).

Two levels of phase time overcurrent element (51P).

Two levels of residual time overcurrent element (51G).

Two levels of ground time overcurrent element (51G).

One level of negative-sequence overcurrent element (51Q).

Phase to ground overvoltage (59G).

Phase to phase overvoltage (59P).

Negative-sequence overvoltage (59Q).

Residual overvoltage (59G).

Phase to ground undervoltage (27G).

Phase to phase undervoltage (27P).

Six levels of secure overfrequency (81O).

Six levels of secure underfrequency (81U).

Two levels of negative power flow with definite time delay (32).

Two levels of positive power flow with definite time delay (32).

Station battery monitoring.

Breaker wear monitoring.

Synchrophasor protocol.

Peak demand and demand metering.

Auto-reclosing.

Creationg fault and disturbance records.

The connection to the experimental circuit is via current transformers with ratio to suit the inputs of the relay.

It allows an effective demonstration of the effect of current and voltage transformer ratio, connection and rating on protective relays.

Accuracy: +- 10%.

Current: 5 A (AC).

Frequency: 50 or 60 Hz.

Operating time: typically 10 ms to 25 ms.

Dimensions: 490 x 330 x 310 mm approx. (19.29 x 12.99 x 12.20 inches approx.). Weight: 10 kg approx. (22 pounds approx.).

• ERP-SDND. Directional/Non Directional Overcurrent Protection Relay.

The Directional/Non Directional Overcurrent Protection Relay, “ERP-SDND”, is used with the Protection Relays Test Base Unit, “ERP-UB”, to enable investigations into protection and monitoring of generator and transformer schemes, overhead lines, underground cables and backup on highvoltage systems.

It enables a wide range of test and investigations and it demonstrates the latest relay technology.

Modern and robust enclosure steel box with carrying handles.

Modern industrial application directional/non directional overcurrent relay presented in an educational and teaching format.

The connections are via safety sockets.

The main functions:

The “ERP-SDND” relay includes numerous phase, negative-sequence, residual-ground, and neutral overcurrent elemnts, as shown in the next table.

| Overcurrent Element Operating Quantity | Number of Elements | Directional Control | Torque Control | Definite-Time Delay |
| --- | --- | --- | --- | --- |
| Maximum phase current (IA, IB, or IC) | 1 inverse-time (51P) 6 instantaneous (50P1-50P6) | Yes Yes, on first 4 | Yes Yes, on first 4 | NA Yes, on first 4 |
| Maximum phase-phase current (IAB, IBC, or ICA) | 4 instantaneous (50PP1-50PP4) | No | No | No |
| Independent phase current | 3 inverse-time (51A, 51B, 51C) | Yes | Yes | NA |
| Residual-ground current (3I0) | 2 inverse-time (51G1,51G2) 6 instantaneous (50G1-50G6) | Yes Yes, on first 4 | Yes Yes, on first 4 | NA Yes, on first 4 |
| Negative-sequence current (3I2) | 1 inverse-time (51Q) 6 instantaneous (50Q1-50Q6) | Yes Yes, on first 4 | Yes Yes, on first 4 | NA Yes, on first 4 |
| Neutral current (IN) | 1 inverse-time (51N) 6 instantaneous (50N1-50N6) | Yes Yes, on first 4 | Yes Yes, on first 4 | NA Yes, on first 4 |

Inverse time overcurrent element settings include a wide and continuous pickup current range, continuous time dial setting  range, and time current curve choices from both US (IEEE) and IEC standard curves shown in the next table.

| IEEE | IEC |
| --- | --- |
| Moderately Inverse (U1) | Standard Inverse (C1) |
| Inverse (U2) | Very Inverse (C2) |
| Very Inverse (U3) | Extremely Inverse (C3) |
| Extremely Inverse (U4) | Long-Time Inverse (C4) |
| Short-Time Inverse (U5) | Short-Time Inverse (C5) |

Undervoltage protection element (27).

Phase overvoltage protection element (59P).

Ground overvoltage protection element (59G).

Negative-sequence overvoltage protection (59Q).

Creating fault and disturbance records.

Selectable blocking.

Selogic control equations.

Event report.

Sequential events recorder.

Breaker wear monitor.

Station battery monitor.

DNP3 Serial LAN/WAN outstation (slave).

Modbus RTU and TPC.

High accuracy metering.

Remote and local control switches.

Star or delta voltage connection.

Synchrophasor measurements.

Fault locator.

Fast SER protocol.

Directional/definite time overcurrent elements.

Two residual ground time overcurrent elements.

Six frequency elements.

Sensitive earth fault protection and directional protection for various system grounding practices.

Load encroachment Logic.

Synchronism check.

ACSELERATOR QuickSet compatible.

The connection to the experimental circuit is via current transformers with ratio to suit the inputs of the relay.

It allows an effective demonstration of the effect of current and voltage transformer ratio, connection and rating on protective relays.

Accuracy: +- 10%.

Current: 5 A (AC).

Frequency: 50 or 60 Hz.

Operating time: typically 10 ms to 25 ms.

Dimensions: 490 x 330 x 310 mm approx. (19.29 x 12.99 x 12.20 inches approx.). Weight: 10 kg approx. (22 pounds approx.).

• ERP-SFT. Overcurrent and Earth Fault Protection Relay.

The Overcurrent and Earth Fault Protection Relay, ”ERP-SFT”, is used with the Protection Relays Test Base Unit, “ERP-UB”, to enable investigations into protection and monitoring of transformers, transmission lines and distribution schemes.

It enables a wide range of test and investigations and it demonstrates the latest relay technology.

Modern and robust enclosure steel box with carrying handles.

Modern industrial application overcurrent and earth fault relay presented in an educational and teaching format.

The connections are made via safety sockets.

The main functions:

Phase instantaneous overcurrent (50P1 – 50P6).

Phase time-overcurrent (51P1T, 51P2T).

Single-phase instantaneous overcurrent (50A, 50B, 50C).

Neutral ground instantaneous overcurrent (50N1, 50N2).

Neutral ground time overcurrent (51N1T).

Residual ground instantaneous overcurrent (50G1, 50G2).

Residual ground time overcurrent (51G1T).

Negative-sequence instantaneous overcurrent (50Q1, 50Q2).

Negative-sequence time overcurrent (51Q1T, 51Q2T).

Setting range, 5 A nominal, instantaneous overcurrent (OFF, 0.5 – 80.0 A).

Setting range, 5 A nominal, time overcurrent (OFF, 0.5 – 16.0 A).

One auto-reclosing function 79.

Selectable blocking.

Circuit monitoring.

Trend, fault and disturbance records.

The connection to the experimental circuit is via current transformers with ratio to suit the inputs of the relay.

It allows an effective demonstration of the effect of current and voltage transformer ratio, connection and rating on protective relays.

Accuracy: +- 5%.

Current: 5 A (AC).

Frequency: 50 or 60 Hz.

Operating time: typically 10 ms to 25 ms.

Dimensions: 490 x 330 x 310 mm approx. (19.29 x 12.99 x 12.20 inches approx.). Weight: 10 kg approx. (22 pounds approx.).

• ERP-PD. Distance Protection Relay.

The Distance Protection Relay, “ERP-PD”, is used with the Protection Relays Test Base Unit, “ERP-UB”, to enable investigations into protection and monitoring of overhead transmission lines and underground cables.

It enables a wide range of test and investigations and it demonstrates the latest relay technology.

Modern and robust enclosure steel box with carrying handles.

Modern industrial application distance protection relay presented in an educational and teaching format.

The connections are via safety sockets.

The main functions:

Two zones of phase Mho distance protection element (21P).

Two zones of ground Mho distance protection element (21G).

Directional phase overcurrent protection element (67P).

Directional ground overcurrent protection element (67G).

Phase overcurrent protection element (50P).

Ground overcurrent protection element (50G).

Phase time overcurrent protection element (51P).

Ground time overcurrent protection element (51G).

Event reports.

Breaker wear monitor.

Fault locator.

Local display.

Synchronophasors.

Load encroachment.

Metering and monitoring functions.

Creating fault and disturbance records.

Blocking of any one protection element.

The connection to the experimental circuit is via current transformers with ratio to suit the inputs of the relay.

It allows an effective demonstration of the effect of current and voltage transformer ratio, connection and rating on protective relays.

Accuracy: +- 10%.

Current: 5 A (AC).

Frequency: 50 or 60 Hz.

Operating time: typically 10 ms to 25 ms.

Dimensions: 490 x 330 x 310 mm approx. (19.29 x 12.99 x 12.20 inches approx.). Weight: 10 kg approx. (22 pounds approx.).

• ERP-CBM. Cybersecurity Application.

The Cybersecurity Application, ”ERP-CBM“, is an access control device that delivers login capability to IED (Intelligent Electronic Devices) or protection relays secured by the cryptographic messages over serial port or Ethernet communication links. This device transmits information via 16 communication ports to the connected protection relays.

The user will be able to access the device web server through the Ethernet F port and to carry out the relevant configurations, such as access permissions, protocols and settings to create its own electrical substation frame.

Power supply: 230 VAC/50 Hz.

Differential magneto-thermal switch, 230 VAC, 30 mA.

ON/OFF switch.

Three Ethernet communication ports.

Two USB communication ports.

16 RS-232 communication ports.

Dimensions: 640 x 320 x 330 mm approx. (25.19 x 12.59 x 12.99 inches approx.). Weight: 20 kg approx. (44 pounds approx.).

• ERP-GMGPT. Motor-Generator with Protection Relays and Automatic Regulation.

The Motor-Generator with Protection Relays and Automatic Regulation, “ERP-GMGPT”, consists of a set of modules whose purpose is to control synchronous generators with independent excitation. Some of these modules have the purpose of regulating the generator excitation current, while others have the purpose of controlling the speed of the generator drive motor. Finally, the ERP-GMGPT also includes a speed/excitation controller which in turn fulfills the function of protecting the motor-generator set.

All these modules are described in their corresponding technical specifications sections.

• GMG4.5K3PH. 4.5 kW Generator-Motor Group.

Motor-generator group coupled in an aluminum frame with wheels.

Generator nominal power: 4.5 kWA.

Generator nominal speed: 3000 rpm.

Generator nominal output current: 6.5 A.

Generator nominal excitation current: 4 A.

Generator power factor: 0.8.

Generator nominal output voltage: 3 x 400 VAC.

Frequency: 50/60 Hz.

Motor nominal power: 5 kVA.

Motor nominal current: 7.2 A.

Motor nominal speed: 3000 rpm.

Dimensions: 1000 x 850 x 400 mm approx. (39.37 x 33.46 x 15.74 inches approx.). Weight: 85 kg approx. (187 pounds approx.)

• N-ERP-PGC01. Generator Protection Relay Module.

The Generator Protection Relay Module, “N-ERP-PGC01”, is a control unit for engine generator simulator system.

The numerous inputs and outputs, along with a modular software frame, allow you to use the N-ERP-PGC01 for a wide range of applications with only a single part number. This includes stand by, AMF (automatic mains failure), peak shaving, import export or distributed generation, among others.

In addition, the N-ERP-PGC01 is compatible with different operating modes such as island operation, parallel island, parallel network and multi-unit parallel grid.

Each part of the N-ERP-PGC01 is correctly identified in order to facilitate operation and fast identification of installation problems.

All the adjustments are executed with the management software from a computer (PC).

Elements of the N-ERP-PGC01:

Power input/output connectors.

Multifunction control and protection device.

Generator group control inputs and outputs connector.

Generator rotor to ground protection Relay.

Isolated operation connector (52GT state and 52G trip command).

Functions:

Prime mover control.

Engine, mains and generator protection.

Engine data measurements.

Generator and mains data measurement:

Voltage, current, power, kVar, kW, kWh, etc.

Load/VAr sharing for up to 32 participants.

Load dependent start/stop.

Automatic, Manual, and Stop operating modes.

Logics Manager for processing measured values, discrete inputs, and internal states.

Engine starter sequencing.

Alarm display with circuit breaker trip and engine shutdown.

AMF (automatic mains failure) standby genset control, with automatic engine start on mains failure detection and open transition breaker control.

Critical mode operation.

Synchronizing (phase matching and slip frequency) and mains parallel operation.

External frequency, voltage, power, and power factor set point control via analogue input or interface.

FIFO (first input first output) event history with 300 entries.

ECU data visualization via J1939.

CAN bus communication to engine controllers, plant management systems, expansion boards, and “toolkit” configuration and visualization  software.

RS-485 Modbus communication with plant management systems.

RS-232 Modbus communication with plant management systems.

Automatic speed and voltage controller:

It enables to connect up to 16 electric generators in parallelisland with active and reactive power distribution and start/stop depending on the load demand.

Enables to connect a generator in parallel with the grid.

It allows different switch control modes, such as opening, closing and synchronization.

Three-phase measurement of the grid and the generator voltage.

Three-phase measurement of the generator intensity and power.

Single-phase measurement of the grid intensity.

Protection system:

Generator: Maximum/minimum voltage (59/27), maximum/minimum frequency (81O/U), voltage asymmetry, detection of dead busbars, overvoltage (32), load unbalance (46), negative-sequence power/reduced power (32R/F), overcurrent by defined curve (50/51), inverse time overcurrent (IEC255), measured ground fault (50N/51N), phase rotation, switches faults.

Network: Maximum/minimum voltage (59/27), maximum/minimum frequency (81O/U), vector jump, phase rotation.

Measurement terminals.

Output terminals for the connection to the lab grid.

2 mm terminals to monitor the PWM for the excitation circuit and speed signals.

Three control switches to:

Start and stop the turbine.

Give permission to synchronize the generator with the grid.

Give permission to synchronize the generator with the national grid.

Two potentiometers to:

Adjust the set point for the generated active power.

Adjust the set point for the voltage.

Emergency stop push button:

Two circuit breakers for synchronization and island mode operations with state indicator lamps.

Dimensions: 640 x 320 x 330 mm approx. (25.19 x 12.59 x 12.99 inches approx.). Weight: 20 kg approx. (44 pounds approx.).

• N-AVR/P. Automatic Voltage Regulator Module.

Input voltage: 0 – 100 VDC.

Input for voltage regulation signal through PWM control.

Terminals for PWM signals monitoring.

Output voltage: 0 – 100 VDC.

DC ammeter for output current measurement, 0 – 4 A.

3-pin female connector for connection to the excitation input of a generator.

Fuse 5 A.

• N-SPAD01. Single-Phase AC/DC Converter Module 1.

0 – 230 VAC single-phase input terminals.

AC/DC rectifier.

DC output terminals.

Filter capacitor for voltage ripple reduction.

Bypass terminals for filter capacitor connection.

Fuse 5 A.

• N-TRANS04. Single-Phase Transformer 230VAC/2x35VAC, 300 VA.

230 VAC single-phase input terminals.

Terminals for a 70 VAC single-phase output.

Terminals for two 35 VAC single-phase outputs.

Two-position switch: 0 (open) / 1 (closed).

Fuses:

Primary side: 2 A.

Secondary side: 5 A.

• All necessary cables to realize the practical exercises are included.

Cables and accessories, for normal operation.

Manuals: This unit is supplied whit the following manuals: Required services, Assembly and Installation, Starting-up, Safety, Maintenance & Practices manuals.

EXERCISES AND PRACTICAL POSSIBILITIES

Practical possibilities with Differential Protection Relay (ERP-PDF):

1.-  Verification of differential protection functionality.

2.-  Transformer differential protection with variable TAP’s voltage regulation.

3.-  Transformer differential protection with different transformer connections.

Practical possibilities with Feeders Management Relay (ERP-MA):

4.-  Verification of the feeder management relay functionality.

5.-  Phase overcurrent element of the feeder management Relay.

6.- Residual ground overcurrent element of the feeder management relay.

7.-  Overvoltage element of the feeder management relay.

Practical possibilities with Directional/Non Directional Overcurrent Protection Relay (ERP-SDND):

8.-  Verification of directional protection functionality.

9.- Directional protection with different measurement circuit conditions.

10.-Directional protection application to transmission line under different load conditions.

Practical possibilities with Overcurrent and Earth Fault Protection Relay (ERP-SFT):

11.-Verification of overcurrent protection functionality.

12.-Verification of phase overcurrent elements.

13.-Verification of residual ground overcurrent elements.

Practical possibilities with Distance Protection Relay (ERP-PD):

14.-Verification of line distance protection functionality.

15.- Line distance protection with different measurement circuit conditions.

16.-Line distance protection with different line loads conditions.

Practical possibilities with Cybersecurity Application (ERP-CBM):

17.-Accessing the cybersecurity protection relay web server.

18.-Creating administrator accounts.

19.- Configuration of the hierarchical communication cybersecurity system between the protection relays using the ACSelerator software.

20.-Creation of users, groups and permissions.

21.-Configuration of the cybersecurity relay communication ports.

22.-Creating communications between different protection relays and the cybersecurity relay.

23.-Creating user passwords with different access levels.

Practical possibilities with Motor-Generator with Protection Relays and Automatic Regulation (ERP-GMGPT):

24.- Island operation with automatic control of the generator-motor group.

25.-Automatic synchronization of the generator with the grid.

26.- Display and control of active power curve during synchronization with the “toolkit” software.

27.- Display and control of active and reactive power curves during synchronization with the “toolkit” software.

Additional practical possibilities with Differential Protection Relay (ERP-PDF):

28.-Verification of phase instantaneous overcurrent protection for winding 1.

29.-Verification of phase definite time-overcurrent protection for winding 1.

30.-Verification of phase inverse time-overcurrent protection for winding 1.

31.-Verification of phase instantaneous overcurrent protection for winding 2.

32.-Verification of phase definite time-overcurrent protection for winding 2.

33.-Verification of phase inverse time-overcurrent protection for winding 2.

34.-Verification of current transformers measurement accuracy.

35.-Power transformer overcurrent protection.

36.-Distribution substation busbar differential protection.

37.-Transmission substation busbar differential protection.

38.-Analysis of event reports and human machine interface.

Additional practical possibilities with Feeders Management Relay (ERP-MA):

39.-Undervoltage element of the feeder management relay.

40.-Verification of phase instantaneous overcurrent protection.

41.-Verification of phase time-overcurrent protection.

42.-Verification of residual overcurrent element.

43.-Verification of residual time-overcurrent element.

44.-Verification of reutral overcurrent element.

45.-Verification of overfrequency protection element.

46.-Verification of underfrequency protection element.

47.-Verification of positive (forward) power flow protection element.

48.-Verification of negative (reverse) power flow protection element.

49.-Protection of distribution feeder example.

50.-Protection of overhead transmission line example.

Additional practical possibilities with Directional/Non Directional Overcurrent Protection Relay (ERP-SDND):

51.-Forward directional protection.

52.-Reverse directional protection.

53.-Non-directional overcurrent protection.

54.-Residual ground time-overcurrent protection.

55.-Residual ground instantaneous overcurrent protection.

56.-Verification of cable undervoltage protection.

57.-Verification of cable overvoltage protection.

58.-Verification of current transformers measurements accuracy.

59.-Verification of voltage transformers measurements accuracy.

60.-Distribution system directional protection.

Additional practical possibilities with Overcurrent and Earth Fault Protection Relay (ERP-SFT):

61.-Verification of phase instantaneous overcurrent protection.

62.-Verification of phase time-overcurrent protection.

63.-Verification of neutral ground instantaneous overcurrent protection.

64.-Verification of neutral ground time-overcurrent protection.

65.- Verification of residual ground instantaneous overcurrent protection.

66.-Verification of residual ground time-overcurrent protection.

67.-Verification of current transformer measurement accuracy.

68.-Power transformer overcurrent protection.

69.-Power transmission line overcurrent protection.

70.-Load feeder overcurrent protection.

71.-Distribution system overcurrent protection.

72.-Power transmission system overcurrent protection.

Additional practical possibilities with Distance Protection Relay (ERP-PD):

73.-Verification of phase instantaneous overcurrent element.

74.-Verification of ground instantaneous overcurrent element.

75.-Verification of phase time-overcurrent protection element.

76.-Verification of ground time-overcurrent protection element.

77.-Verification of current transformer measurement accuracy.

78.-Verification of current transformers connection diagram.

79.-Verification of voltage transformers measurement cccuracy and connection diagram for distance protection.

80.-Overhead transmission line parameters estimation for distance protection.

81.- Overhead transmission line distance protection.

82.- Distance protection event reports analysis.

83.- Distance protection relay human machine interface.

84.- Distance protection relay configuration.

85.- Distance protection of simple power system example.

Additional practical possibilities with Cybersecurity Application (ERP-CBM):

86.- Resetting the protection relay to set up the communication system from scratch.

87.-Simulation of cyber attack.

88.- Creation of encrypted communication between the cybersecurity relay and the differential protection relay.

89.- Creation of encrypted communication between the cybersecurity relay and the overcurrent protection relay.

90.- Creation of encrypted communication between the cybersecurity relay and the distance protection relay.

91.- Creation of encrypted communication between the cybersecurity relay and the directional protection relay.

92.- Creation of encrypted communication between the cybersecurity relay and the feeder management relay.

Additional practical possibilities with Motor-Generator with Protection Relays and Automatic Regulation (ERP-GMGPT):

93.- Working of motor protection switch.

94.- Motor protection relay.

95.- Thermistor protection.

96.- Investigation of time overcurrent protection.

97.- Unbalanced load protection.

98.- Reverse power protection.

99.- Overvoltage and undervoltage protection.

100.-Stator earth-fault protection.

101.-Generator differential protection (optional with ERP-PDF).

102.-Rotor earth-fault protection.

- Several other exercises can be done and designed by the user.

Optional

ERP/ICAI. Interactive Computer Aided Instruction Software:

This complete software package consists of an Instructor Software (EDIBON Classroom Manager - ECM-SOF) totally integrated with the Student Software (EDIBON Student Labsoft - ESL-SOF). Both are interconnected so that the teacher knows at any moment what is the theoretical and practical knowledge of the students.

- ECM-SOF. EDIBON Classroom Manager (Instructor Software).

ECM-SOF is the application that allows the Instructor to register students, manage and assign tasks for workgroups, create own content to carry out Practical Exercises, choose one of the evaluation methods to check the Student knowledge and monitor the progression related to the planned tasks for individual students, workgroups, units, etc... so the teacher can know in real time the level of understanding of any student in the classroom.

Innovative features:

• User Data Base Management.

• Administration and assignment of Workgroup, Task and Training sessions.

• Creation and Integration of Practical Exercises and Multimedia Resources.

• Custom Design of Evaluation Methods.

• Creation and assignment of Formulas & Equations.

• Equation System Solver Engine.

• Updatable Contents.

• Report generation, User Progression Monitoring and Statistics.

- ESL-SOF. EDIBON Student Labsoft (Student Software).

ESL-SOF is the application addressed to the Students that helps them to understand theoretical concepts by means of practical exercises and to prove their knowledge and progression by performing tests and calculations in addition to Multimedia Resources. Default planned tasks and an Open workgroup are provided by EDIBON to allow the students start working from the first session. Reports and statistics are available to know their progression at any time, as well as explanations for every exercise to reinforce the theoretically acquired  technical knowledge.

Innovative features:

• Student Log-In & Self-Registration.

• Existing Tasks checking & Monitoring.

• Default contents & scheduled tasks available to be used from the first session.

• Practical Exercises accomplishment by following the Manual provided by EDIBON.

• Evaluation Methods to prove your knowledge and progression.

• Test self-correction.

• Calculations computing and plotting.

• Equation System Solver Engine.

• User Monitoring Learning & Printable Reports.

• Multimedia-Supported auxiliary resources.