TENDER SPECIFICATIONS (for main items)

1 MPGDC. Unit:

• Low voltage switchgear for the coupling maneuver of the generator sets.

Rated voltage: 400 VAC+N+GND.

• Medium voltage switchgear for the power supply of the propulsion system.

Rated voltage: 12 kV+N+GND.

• Two three-phase generator sets.

Four-stroke diesel engine with in-line cylinders.

Liquid cooled.

Forced lubrication.

Water pump.

Injection system: indirect (IDI).

Rated Power (kW/HP): 10 kW/13 HP.

Diesel fuel.

Dry weight (kg): 85.

Air filter.

Synchronous generator:

Synchronous speed: 1500 rpm.

Nominal frequency: 50 Hz or 60 Hz (according to ordered reference).

Apparent power: 8 kVA.

Rated voltage: 400 VAC.

Rated current: 11 A.

Power factor: 0.8. Number of poles: 4.

Rated current excitation: 1.5 A.

Rated voltage excitation: 23.7 A.

• Power Management System (PMS).

This is a PMS system that monitors the power flows of the electric generators and sends the necessary commands for starting/stopping the gensets for proper control of the gensets.

• Power controllers for the generator sets.

These controllers include algorithms and logic specifically designed to start, stop, control and protect the genset, circuit breaker and power grid, if applicable. This technology enables the standardization of distributed power generation applications. These applications can range from stand-alone emergency backup power to parallel load sharing of multiple gensets in complex, segmented distribution systems with multiple mains feeds and circuit breakers.

These controllers are in turn protections for:

Overvoltage protection.

Overcurrent protection.

Reverse power protection.

Over and under frequency protection.

• Three-phase hybrid inverter for the uninterruptible power supply system.

Three-phase inverter.

Rated power: 6 kW.

Battery charge/discharge control.

• High voltage battery for the uninterruptible power supply system.

LiPeFo battery.

Stored energy: 5 kWh.

BMS.

• Network analyzers for measuring the ship’s power flows with data acquisition.

The network analyzer module allows fulfilling measurements, displaying and analyzing all the parameters of the AC electrical networks. It has an LCD screen and push-buttons for the navigation through the different menus. It includes specific software for monitoring current and voltage curves, harmonics display, tariffs programming, alarms programming and electrical parameters storage.

Features:

Multifunctional three-phase power meter:

Single and three-phase voltage. Up to 690 VAC L-L.

Line and neutral nominal current: 10 A.

Active, reactive and apparent power.

Suitable frequencies: 25 Hz, 50 Hz, 60 Hz y 400 Hz.

Display of the V-I vector diagram.

Supply voltage: 85 - 265 VAC.

Energy quality control:

Current and voltage individual harmonics measurement. Up to the 40th harmonic.

Voltage and current THD, TDD & K-factor.

Maximums and minimums display.

Waveforms display, 128 samples/sec.

Events and data storage:

Harmonics analyzer:

Voltage and current THD, current TDD and K-Factor, up to the 40th harmonic.

Current and voltage harmonic spectrum and angles.

Tariff programming:

Class 0.5S IEC 62053 - 22, active and reactive power in four quadrants.

Measurement of the total and per phase three-phase active, reactive and apparent powers.

Usage time, four energy/demand records of total tariffs.

Eight tariffs, four seasons, four types of days.

Automatic daily report of energy consumption maximums and minimums.

Communications:

RS-485 communication port.

• Two high power frequency inverters for the ship’s turbine propulsion system.

Rated power: 3 kW.

PWM output voltage connections: Three-phase: 400 VAC.

Digital inputs control panel: 5 configurable digital inputs.

Analog inputs control panel:

0 - 10 V analog input for speed control.

4 - 20 mA analog input for speed control.

10 K, potentiometer for speed control of induction motor.

Two relay outputs for alarm configuration: 2 NO/NC outputs. 50 mA.

Two transistor outputs for alarm configuration.

Display for setting and visualization of machine parameters.

• Three-phase squirrel cage induction motors for propulsion simulation.

Rated power: 3000 W.

Rated voltage: 3 x 230/400 VAC Δ/Y.

Frequency: 50/60 Hz.

Number of poles: 2.

Speed: 2730 rpm.

• Braking system for propulsion load simulation.

Magnetic brake.

Rated voltage: 400 VAC.

Rated speed: 3000 rpm.

Analog signal to control the braking force.

• Three-phase resistive loads to simulate active power consumption.

Three-phase motorized resistor of 3000 W.

• Three-phase isolation transformer for simulation of medium voltage and low voltage bus bars.

Input voltage: 400 VAC.

Output voltage: 690 VAC.

Rated power: 6 kVA.

• Water reserve tank for the cooling system of the generator sets.

Water pump.

Water pump speed controller.

Water reserve tank.

Heat exchanger.

• High-voltage protection unit: gloves, pole, goggles, etc.

• Fire extinguisher.

• All necessary cables to realize the practical exercises are included.

The complete unit includes as well:

Advanced Real-Time SCADA.

Open Control + Multicontrol + Real-Time Control.

Specialized EDIBON Control Software based on LabVIEW.

National Instruments Data Acquisition board (250 KS/s, kilo samples per second).

Calibration exercises, which are included, teach the user how to calibrate a sensor and the importance of checking the accuracy of the sensors before taking measurements.

Projector and/or electronic whiteboard compatibility allows the unit to be explained and demonstrated to an entire class at one time.

Capable of doing applied research, real industrial simulation, training courses, etc.

Remote operation and control by the user and remote control for EDIBON technical support, are always included.

Totally safe, utilizing 4 safety systems (Mechanical, Electrical, Electronic & Software).

Designed and manufactured under several quality standards.

Optional ICAI software to create, edit and carry out practical exercises, tests, exams, calculations, etc. Apart from monitoring user's knowledge and progress reached.

This unit has been designed for future expansion and integration. A common expansion is the EDIBON Scada-Net (ESN) System which enables multiple students to simultaneously operate many units in a network.

2 MPGDC/CCSOF. Computer Control +Data Acquisition+Data Management Software:

The three softwares are part of the SCADA system.

Compatible with the industry standards.

Flexible, open and multicontrol software, developed with actual windows graphic systems, acting simultaneously on all process parameters.

Management, processing, comparison and storage of data.

Sampling velocity up to 250 KS/s (kilo samples per second).

Calibration system for the sensors involved in the process.

It allows the registration of the alarms state and the graphic representation in real time.

Open software, allowing the teacher to modify texts, instructions. Teacher’s and student’s passwords to facilitate the teacher’s control on the student, and allowing the access to different work levels.

This unit allows the 30 students of the classroom to visualize simultaneously all the results and the manipulation of the unit, during the process, by using a projector or an electronic whiteboard.

3 Cables and Accessories, for normal operation.

4 Manuals:

This unit is supplied with 8 manuals: Required Services, Assembly and Installation, Control Software, Starting-up, Safety, Maintenance, Calibration & Practices Manuals.

*	References 1 to 4 are the main items: MPGDC + MPGDC/CCSOF + Cables and Accessories + Manuals are included in the minimum supply for enabling normal and full operation.

EXERCISES AND PRACTICAL POSSIBILITIES TO BE DONE WITH THE MAIN ITEMS

1.-	Assembly of low voltage breaking and switching cubicles.

2.-	Assembly of high voltage breaking and disconnecting switchgear.

Performing the main switching and disconnecting operations in the low voltage busbar for future maintenance and revisions.

4.-	Carrying out of the main switching and disconnection maneuvers in the medium voltage busbar for future maintenance and revisions.

5.-	Connection of the generator sets to the low voltage switchgear. First verifications before start-up.

6.-	Identification and configuration of auxiliary circuits and sensitive devices.

7.-	Commissioning of the first generating set. Identification of the line voltages and monitoring of the power circuit for correct operation.

8.-	Closing of the circuit breaker of the generator 1 low voltage switchgear. Identification of the line voltages up to the medium voltage switchgear.

9.-	Closing of the generator 1 medium voltage switchgear. Identification of the line voltages up to the power supply to the ship’s electric thrusters.

10.-	Start-up of the second generator set. Identification of the line voltages and monitoring of the power circuit for correct operation.

11.-	Closing of the generator 2 low voltage switchgear. Verification of the correct coupling of generators 1 and 2.

12.- Analysis of the load sharing with both generators working in parallel.

13.- Analysis and configuration of operating priorities in the diesel generators. Configuration of generator 2 as standby.

14.-	Creation of failure scenarios: failure of generator 1 and start-up of generator 2, failure of both generators and connection of the UPS system to the low voltage busbar.

15.- Study of the steps to follow for the restoration of the electrical system after a blackout.

16.- Connection of the low voltage busbar to the electrical network.

Other possibilities to be done with this unit:

17.- Many students view results simultaneously.

To view all results in real time in the classroom by means of a projector or an electronic whiteboard.

18.- The Computer Control System with SCADA allows a real industrial simulation.

19.- This unit is totally safe as uses mechanical, electrical/electronic, and software safety devices.

20.- This unit can be used for doing applied research.

21.- This unit can be used for giving training courses to Industries even to other Technical Education Institutions.

22.- Visualization of all the sensors values used in the MPGDC unit process.

- Several other exercises can be done and designed by the user.

TENDER SPECIFICATIONS (for optional items)

a) Technical and Vocational Education configuration

5 MPGDC/ICAI. Interactive Computer Aided Instruction Software.

This complete software package consists of an Instructor Software (EDIBON Classroom Manager - ECM-SOF) totally integrated with the Student Software (EDIBON Student Labsoft - ESL-SOF). Both are interconnected so that the teacher knows at any moment what is the theoretical and practical knowledge of the students.

- ECM-SOF. EDIBON Classroom Manager (Instructor Software).

ECM-SOF is the application that allows the Instructor to register students, manage and assign tasks for workgroups, create own content to carry out Practical Exercises, choose one of the evaluation methods to check the Student knowledge and monitor the progression related to the planned tasks for individual students, workgroups, units, etc...so the teacher can know in real time the level of understanding of any student in the classroom.

Innovative features:

• User Data Base Management.

• Administration and assignment of Workgroup, Task and Training sessions.

• Creation and Integration of Practical Exercises and Multimedia Resources.

• Custom Design of Evaluation Methods.

• Creation and assignment of Formulas & Equations.

• Equation System Solver Engine.

• Updatable Contents.

• Report generation, User Progression Monitoring and Statistics.

- ESL-SOF. EDIBON Student Labsoft (Student Software).

ESL-SOF is the application addressed to the Students that helps them to understand theoretical concepts by means of practical exercises and to prove their knowledge and progression by performing tests and calculations in addition to Multimedia Resources. Default planned tasks and an Open workgroup are provided by EDIBON to allow the students start working from the first session. Reports and statistics are available to know their progression at any time, as well as explanations for every exercise to reinforce the theoretically acquired technical knowledge.

Innovative features:

• Student Log-In & Self-Registration.

• Existing Tasks checking & Monitoring.

• Default contents & scheduled tasks available to be used from the first session.

• Practical Exercises accomplishment by following the Manual provided by EDIBON.

• Evaluation Methods to prove your knowledge and progression.

• Test self-correction.

• Calculations computing and plotting.

• Equation System Solver Engine.

• User Monitoring Learning & Printable Reports.

• Multimedia-Supported auxiliary resources.

b) Multipost Expansions options

6 MINI ESN. EDIBON Mini Scada-Net System for being used with EDIBON Teaching Units.

MINI ESN. EDIBON Mini Scada-Net System allows up to 30 students to work with a Teaching Unit in any laboratory, simultaneously.

The MINI ESN system consists of the adaptation of any EDIBON Computer Controlled Unit with SCADA integrated in a local network.

This system allows to view/control the unit remotely, from any computer integrated in the local net (in the classroom), through the main computer connected to the unit.

Main characteristics:

- It allows up to 30 students to work simultaneously with the EDIBON Computer Controlled Unit with SCADA, connected in a local net.

- Open Control + Multicontrol + Real Time Control + Multi Student Post.

- Instructor controls and explains to all students at the same time.

- Any user/student can work doing "real time" control/multicontrol and visualisation.

- Instructor can see in the computer what any user/student is doing in the unit.

- Continuous communication between the instructor and all the users/students connected.

Main advantages:

- It allows an easier and quicker understanding.

- This system allows you can save time and cost.

- Future expansions with more EDIBON Units.

The system basically will consist of:

This system is used with a Computer Controlled Unit.

- Instructor’s computer.

- Students’ computers.

- Local Network.

- Unit-Control Interface adaptation.

- Unit Software adaptation.

- Webcam.

- MINI ESN Software to control the whole system.

- Cables and accessories required for a normal operation.