TENDER SPECIFICATIONS

Anodized aluminum structure and panel made of painted steel.

The unit includes wheels to facilitate its mobility.

Main metallic elements made of stainless steel.

Diagram in the front panel with distribution of the elements similar to the real one.

Duct:

Material: stainless steel.

Length: 1900 mm approx.

It includes two transparent windows: one is located in the left side to visualize the humidification and dehumidification processes and

the other is located in the front side to allow the access for students to take readings and to change the instruments.

The duct includes different elements to adjust the air humidity:

Humidifier:

Type: ultrasonic atomizer.

Minimum water level: 45 mm.

Low water cut-off.

Dehumidifier:

Peltier cooling element.

Cooling capacity: 74.5 W.

It includes a heat sink. Thermal resistance: 0.75 K/W

Fan to show the effects of airflow on different instruments and to ensure a good mixing. Maximum air flow rate: 380 m³/h, max. speed: 2760 rpm.

Orifice plate located at the fan outlet.

Inclined manometer to measure the pressure drop in the orifice plate. Range: 0 - 3" WC.

Three regulations valves to work with the unit in two configurations (the air can be recycled inside of the duct or taken from the room air) and to change the airflow rate:

One is situated in the right side of the duct.

Another is situated between the right side of the duct and the room air inlet.

Finally, the last valve is situated in the room air inlet.

Measuring methods for air humidity measurement:

Wet and dry bulb hygrometer, range: - 5…50°C, precision: ±0.5%.

Hair hygrometer, range: 0 - 100% R.H.

Capacitive humidity sensor, range: 0 - 100% R.H.

Humidity sensor with synthetic fiber and combined temperature sensor. Humidity range: 30 - 100% R.H. Temperature range: 5 - 80°C.

Electronic console:

Metallic box.

Humidity sensor with synthetic fiber and temperature sensor connector.

Capacitive humidity sensor connector.

ON/OFF controller for the humidifier.

ON/OFF controller for the dehumidifier.

ON/OFF controller for the fan.

Fan speed controller.

Two digital displays for the temperature and the humidity for the humidity sensor with synthetic fiber and temperature sensor.

Digital display for the capacitive humidity sensor.

Digital display for the speed of the fan.

Cables and accessories, for normal operation.

Manuals:

This unit is supplied with the following manuals: Required services, Assembly and Installation, Starting-up, Safety, Maintenance and Practices manual.

Unit: - Dimensions: 2400 x 700 x 1600 mm approx. (94.48 x 27.56 x 62.99 inches approx.) - Weight: 80 Kg approx. (176.3 pounds approx.).

Electronic console: - Dimensions: 490 x 330 x 310 mm approx. (19.29 x 12.99 x 12.20 inches approx.) - Weight: 10 Kg approx. (22 pounds approx.).

EXERCISES AND PRACTICAL POSSIBILITIES

1.- 	Study of different measuring methods for air humidity: hair hygrometer, humidity sensor with synthetic fiber, capacitive humidity sensor and wet and dry bulb hygrometer.

2.- 	Calculation of the flow with the orifice plate.

3.- 	Study of the state of the air humidity sensor in the h-x diagram (psychometric chart).

4.- 	Determination of the room air humidity using different types of instruments.

5.- 	Determination of the air humidity using different types of instruments and varying the humidity of the air with a humidifier and a dehumidifier.

6.- 	Comparison of different measuring methods for accuracy and ease of use.

7.- 	Study of the effect of the fan flow rate in the humidity measurement of the air room.

8.- 	Study of the effect of the fan flow rate in the humidity measurement of the air and varying the humidity of the air with a humidifier and a dehumidifier.

Optional

TMHA/ICAI. Interactive Computer Aided Instruction Software:

This complete software package consists of an Instructor Software (EDIBON Classroom Manager - ECM-SOF) totally integrated with the Student Software (EDIBON Student Labsoft - ESL-SOF). Both are interconnected so that the teacher knows at any moment what is the theoretical and practical knowledge of the students.

- ECM-SOF. EDIBON Classroom Manager (Instructor Software).

ECM-SOF is the application that allows the Instructor to register students, manage and assign tasks for workgroups, create own content to carry out Practical Exercises, choose one of the evaluation methods to check the Student knowledge and monitor the progression related to the planned tasks for individual students, workgroups, units, etc... so the teacher can know in real time the level of understanding of any student in the classroom.

Innovative features:

• User Data Base Management.

• Administration and assignment of Workgroup, Task and Training sessions.

• Creation and Integration of Practical Exercises and Multimedia Resources.

• Custom Design of Evaluation Methods.

• Creation and assignment of Formulas & Equations.

• Equation System Solver Engine.

• Updatable Contents.

• Report generation, User Progression Monitoring and Statistics.

- ESL-SOF. EDIBON Student Labsoft (Student Software).

ESL-SOF is the application addressed to the Students that helps them to understand theoretical concepts by means of practical exercises and to prove their knowledge and progression by performing tests and calculations in addition to Multimedia Resources. Default planned tasks and an Open workgroup are provided by EDIBON to allow the students start working from the first session. Reports and statistics are available to know their progression at any time, as well as explanations for every exercise to reinforce the theoretically acquired  technical knowledge.

Innovative features:

• Student Log-In & Self-Registration.

• Existing Tasks checking & Monitoring.

• Default contents & scheduled tasks available to be used from the first session.

• Practical Exercises accomplishment by following the Manual provided by EDIBON.

• Evaluation Methods to prove your knowledge and progression.

• Test self-correction.

• Calculations computing and plotting.

• Equation System Solver Engine.

• User Monitoring Learning & Printable Reports.

• Multimedia-Supported auxiliary resources.